## Slide 1: Lecture No. 27 Flue Gases
At the end of this lecture, students will be able to:
  Explain flue gases
  Identify the sources of flue gases
  Discuss the disadvantages of flue gases
  Control measures

## Slide 2: Flue Gases
Flue gas : gas that exits to the atmosphere via a flue, which is a pipe or channel for conveying exhaust gases from a fireplace, oven, furnace, boiler or steam generator
Sources: Burning of Fossil fuel to obtain energy, Manufacturing Industries like Paints, Chemicals, Agrochemicals, Leather, etc release flue gases
Pollutants expelled out: oxides of nitrogen, sulphur, carbon, and particulate matter, water vapor

## Slide 3
Effect of Flue gas
Emission of SOx one of the major causes of acid precipitation

## Slide 4: Flue gases effect
Gases settle in the Boilers, chimneys, other machinery parts
Environmental problems like pollutants entering into food web, global warnings, acid rains, farming issues
Depletion of ozone layer, climatic conditions etc., making a unsafe earth
Acid rain -emissions of sulfur dioxide & nitrogen oxide, which react with the water molecules in the atmosphere to produce acids

## Slide 5
Fossil fuels such as coal and oil contain a significant amount of sulfur
Fossil fuels when burnt, about 95 % of the sulfur is converted to SO2
SO2 + (Excess of O2) → SO3
High gas temperature (800 °C) favors formation of SO3
SO3 can be formed through catalysis by metals in the fuel
In whatever way SO3 is formed, it does not behave like SO2
It forms a liquid aerosol known as sulfuric acid (H2SO4) mist, that is very difficult to remove
Sulfuric acid mist is often the cause of the blue haze that often appears as the flue gas plume dissipates. This problem is being addressed by the use of wet electrostatic precipitators
SOX CONTROL

## Slide 6: General methods to control SOX
Change to Low Sulfur Fuel
  Natural Gas
  Liquefied Natural Gas
  Low Sulfur Oil
  Low Sulfur Coal
Use Desulfurized Coal and Oil Increase Effective Stack Height
  Build Tall Stacks
  Redistribution of Stack Gas Velocity Profile
  Modification of Plume Buoyancy

## Slide 7: General methods to control SOX
Use Flue Gas Desulfurization Systems
Use Alternative Energy Sources,
such as Hydro-Power or Nuclear-Power

## Slide 8: Flue Gas Desulfurization
SO2 scrubbing, or Flue Gas Desulfurization processes can be classified as:
  Throwaway or Regenerative, depending upon whether the recovered sulfur is discarded or recycled
  Wet or Dry, depending upon whether the scrubber is a liquid or a solid

## Slide 9: Dry scrubbing and wet scrubbing system

## Slide 10: Flue Gas Desulfurization
Flue Gas Desulfurization Processes
The major flue gas desulfurization ( FGD ), processes are :
  Limestone Scrubbing
  Lime Scrubbing
  Dual Alkali Processes
  Lime Spray Drying
  Wellman-Lord Process
Flue Gas Desulfurization process at Great Plains Synfuels Pl

## Slide 11: Limestone Scrubbing
Limestone slurry is sprayed on the incoming flue gas
Sulfur dioxide gets absorbed
    CaCO3 + H2O + 2SO2 ----> Ca+2 + 2HSO3-+ CO2
    CaCO3 + 2HSO3-+ Ca+2 ----> 2CaSO3 + CO2 + H2O

## Slide 12: Lime Scrubbing
Lime Scrubbing offers better utilization of the reagent
Operation is more flexible
CaO + H2O -----> Ca(OH)2
SO2 + H2O <----> H2SO3
H2SO3 + Ca(OH)2 -----> CaSO3.2 H2O
CaSO3.2 H2O + (1/2)O2 -----> CaSO4.2 H2O

## Slide 13: Disadvantages of lime and lime stone scrubbing system
Major disadvantage is the high cost of lime compared to limestone
Lime and Limestone scrubbing lead to deposits inside spray tower.
  Deposits can lead to plugging of the nozzles through which the scrubbing slurry is sprayed

## Slide 14: Dual Alkali System
  Dual Alkali system uses two regents to remove the sulfur dioxide
  Sodium sulfite / Sodium hydroxide are used for the absorption of sulfur dioxide inside the spray chamber
  Resulting sodium salts are soluble in water, so no deposits are formed
  Water spray is treated with lime or limestone, along with make-up sodium hydroxide or sodium carbonate
  Sulfite / sulfate ions are precipitated, and the sodium hydroxide is regenerated

## Slide 15: Lime – Spray Drying
  Lime Slurry is sprayed into the chamber
  Sulfur dioxide is absorbed by the slurry
  Liquid-to-gas ratio is maintained such that the spray dries before it reaches the bottom of the chamber
  Dry solids are carried out with the gas, and are collected in fabric filtration unit
System needs lower maintenance, lower capital costs, and lower energy usage

## Slide 16: Wellman – Lord Process
Schematic process flow diagram – SO2 scrubbing and recovery system

## Slide 17: Wellman – Lord Process

## Slide 18: Wellman – Lord Process…
In this process, sulfur dioxide from flue gas is absorbed in a sodium sulfite solution in water forming sodium bisulfite; other components of flue gas are not absorbed
After lowering the temperature the bisulfite is converted to the sodium persulfite which precipitates
Notes: Na2O8S2 sodium perosulfite

## Slide 19: Wellman – Lord Process
Process consists of the following sub processes:
  Flue gas pre-treatment
  Sulfur dioxide absorption by sodium sulfite
  Purge treatment
  Sodium sulfite regeneration
  The concentrated sulfur dioxide stream is processed to a marketable product.
Flue gas is pre - treated to remove the particulate. The sodium sulfite neutralizes the sulfur dioxide :
Na2SO3 + SO2 + H2O -----> 2NaHSO3
Sodium sulphite sodium bisulphite
Notes: Sodium sulfite is a soluble sodium salt of sulfurous acid with the chemical formula Na₂SO₃. It is a product of sulfur dioxide scrubbing, a part of the flue-gas desulfurization process

## Slide 20: Wellman – Lord Process
Some of the Na2SO3 reacts with O2 and the SO3 present in the flue gas to form Na2SO4 and NaHSO3
Sodium sulfate does not help in the removal of sulfur dioxide, and is removed
Part of the bisulfate stream is chilled to precipitate the remaining bisulfate and remaining bisulfate stream is evaporated to release the sulfur dioxide, and regenerate the bisulfite

## Slide 21: NOX CONTROL Background on Nitrogen Oxides
  NO nitric oxide
  NO2 nitrogen-di-oxide
  NO3 nitrate
  N2O dinitrogen monoxide
  N2O3 dinitrogen trioxide
  N2O4 dinitrogen tetraoxide
  N2O5 dinitrogen pentaoxide
NO and NO2 are the most common of the seven oxides listed above NOx released from stationary sources is of two types

## Slide 22: General Methods For Control of NOx Emissions
NOx control can be achieved by:
  Fuel Denitrogenation
  Combustion Modification
  Modification of operating conditions
  Tail-end control equipment
    Selective Catalytic Reduction
    Selective Non - Catalytic Reduction
    Electron Beam Radiation
    Staged Combustion

## Slide 23: Fuel Denitrogenation
  One approach of fuel denitrogenation is to remove a large part of the nitrogen contained in the fuels
  Nitrogen is removed from liquid fuels by mixing the fuels with hydrogen gas, heating the mixture and using a catalyst to cause nitrogen in the fuel and gaseous hydrogen to unite. This produces ammonia and cleaner fuel
  Reduce the nitrogen contained in both
  naturally occurring and synthetic fuels

## Slide 24: Combustion Modification
Combustion control uses one of the following strategies:
  Reduce peak temperatures of the flame zone. The methods are :
      increase the rate of flame cooling
      decrease the adiabatic flame temperature by dilution
  Reduce residence time in the flame zone. For this we change the shape of the flame zone
  Reduce Oxygen concentration in the flame one. This can be accomplished by:
      decreasing the excess air
      controlled mixing of fuel and air
      using a fuel rich primary flame zone

## Slide 25: Selective Catalytic Reduction (SCR)
Schematic process flow diagram – NOX control

## Slide 26: Electron Beam Radiation
This treatment process is under development, and is not widely used
Irradiation of flue gases containing NOx or SOx produce nitrate and sulfate ions
      The addition of water and ammonia produces NH4NO3, and (NH4)2SO4
      The solids are removed from the gas, and are sold as fertilizers

## Slide 27: Formation of Carbon Monoxide
Due to insufficient oxygen
Factors affecting Carbon monoxide formation:
        Fuel-air ratio
        Degree of mixing
        Temperature
Carbon Monoxide Control

## Slide 28: Sources of Carbon Dioxide
Human-Related Sources
Combustion of fossil fuels: Coal, Oil, and Natural Gas in power plants, automobiles, and industrial facilities
Use of petroleum-based products
Industrial processes: Iron and steel production, cement, lime, and aluminum manufactures
Natural Sources
Volcanic eruptions
Ocean-atmosphere exchange
Plant photosynthesis

## Slide 29: General methods for control of CO emissions
Stationary Sources
      Proper Design
      Installation
      Operation
      Maintenance
Process Industries
      Burn in furnaces or waste heat boilers

## Slide 30: General methods for control of CO2 emissions
Reducing energy consumption, increasing the efficiency of energy conversion
Switching to less carbon intensive fuels
Increasing the use of renewable sources
Sequestering CO2 through biological, chemical, or physical processes

## Slide 31: Industrial Sources of Particulate Emissions
Iron & Steel Mills, the blast furnaces, steel making furnaces
Petroleum Refineries, the catalyst regenerators, air-blown asphalt stills, and sludge burners
Portland cement industry, Asphalt batching plants
Production of sulfuric acid, Production of phosphoric acid
Soap and Synthetic detergent manufacturing
Glass & glass fiber industry
Nuclear power stations
Particulate Matter Control

## Slide 32: Effects of particulate emissions
Primary Effects
Reduction of visibility
  size distribution and refractive index of the particles
  direct absorption of light by particles
  direct light scattering by particles
  limit - 150 g / m3 concentration ~ average visibility of 5 miles
  ( satisfactory for air and ground transportation )
  threshold limit is 200 - 250 g / m3 ( dust )
  levels of 400 - 500 g / m3 considered as nuisance

## Slide 33: General methods for control of particulate emissions
Five basic types of dust collectors :
Gravity and Momentum collectors
  Settling chambers, baffle chambers
Centrifugal Collectors
  Cyclones
  Mechanical centrifugal collectors
Fabric Filters
  Bag houses
  Fabric collectors

## Slide 34: General methods for control of particulate emissions
Electrostatic Precipitators
  Tubular
  Plate
  Wet
  Dry
  Wet Collectors
  Spray towers
  Impingement scrubbers
  Wet cyclones
  Peaked towers
  Mobile bed scrubbers

## Slide 35: Summary
  Flue gases: Nox, Sox, CO, CO2
  Sources of flue gases: Industries, Domestic, Thermal power plants, autombiles
  Measures to control them: Desulphurization, denitrogenation
  Control of Particulate matter: Gravity settlers, centrifugal filters, fabric filters